## Wind
Hazard Variable | Infrastructure Component | Lognormal Distribution (y/n) | Best Fit (y/n) | 1st Additional Variables | 2nd Additional Vriable | 3rd Additional Variable | 4th Additional Variable | Mu (if lognormal distribution) | Sigma (if lognormal distribution) | Alternate Equation | Source
Wind Gust Speed (m/s) | Substation | y | n | Terrain type 1 | Moderate |  |  | 4.921 | 0.148 |  | Ouyang, M., & Duenas-Osorio, L. (2014). Multi-dimensional hurricane resilience assessment of electric power systems. Structural Safety, 48, 15-24.
|  |  |  | Terrain type 1 | Severe |  |  | 5.06 | 0.15
|  |  |  | Terrain type 1 | Complete |  |  | 5.428 | 0.163
|  |  |  | Terrain type 2 | Moderate |  |  | 4.947 | 0.122
|  |  |  | Terrain type 2 | Severe |  |  | 5.094 | 0.124
|  |  |  | Terrain type 2 | Complete |  |  | 5.337 | 0.127
|  |  |  | Terrain type 3 | Moderate |  |  | 4.998 | 0.128
|  |  |  | Terrain type 3 | Severe |  |  | 5.141 | 0.132
|  |  |  | Terrain type 3 | Complete |  |  | 5.419 | 0.149
|  |  |  | Terrain type 4 | Moderate |  |  | 5.044 | 0.138
|  |  |  | Terrain type 4 | Severe |  |  | 5.185 | 0.139
|  |  |  | Terrain type 4 | Complete |  |  | 5.478 | 0.119
|  |  |  | Terrain type 5 | Moderate |  |  | 5.068 | 0.136
|  |  |  | Terrain type 5 | Severe |  |  | 5.204 | 0.147
|  |  |  | Terrain type 5 | Complete |  |  | 5.523 | 0.132
Wind Gust Speed (mph) | Transmission Lines | n | n | [6 empty] | #VALUE! | "Cost benefit analysis of the deployment of utility infrastructure upgrades and storm hardening programs", 2009.
Wind Gust Speed (mph) | Distribution Poles | n | n | [6 empty] | #VALUE! | "Cost benefit analysis of the deployment of utility infrastructure upgrades and storm hardening programs", 2009.
Wind speed (m/s) | Solar Panels | y | n |  |  |  |  | 4.0604 | 0.3 |  | L Ceferino, N Lin, D Xi. 2021. “Stochastic Modeling of Solar Generation During Hurricanes.” PREPRINT (Version 1) available at Research Square https://doi.org/10.21203/rs.3.rs-797974/v1
Wind speed (m/s) | Transmission Towers (Greece) | y | y |  |  |  |  | 3.628 | 0.1158 |  | D V Bilionis, D Vamvatsikos. 2019. “Wind performance assessment of telecommunication towers: A case study in Greece.” Eccomas Proceedia COMPDYN (2019) 5741-5755. DOI: https://oa.mg/work/10.7712/120119.7342.19629
Wind Gust Speed (mph) | Coal Power Plant | y | y |  |  |  |  | 5.058 | 0.122 |  | E B Watson, A H Etemadi. 2020. "Modeling Electrical Grid Resilience Under Hurricane Wind Conditions With Increased Solar and Wind Power Generation." IEEE Transactions on Power Systems 352(2020) pp. 929-937. https://doi.org/10.1109/TPWRS.2019.2942279
| Gas Power Plant | y | y |  |  |  |  | 5.205 | 0.089
| Solar Power Plant | y | y |  |  |  |  | 5.102 | 0.136
| Wind Power Plant | y | y |  |  |  |  | 5.073 | 0.124
| Nuclear Power Plant | y | y |  |  |  |  | 6.056 | 0.217
Wind gust speed (m/s) | Wood Utility Pole (class 1) | y | n | age=5 #choose between 0 and 100 | wind_direction=60 #choose between 0 and 90 degrees | conductor_area=3 #choose between 0 and 8 (calculated as a product of number and diameter of pole, span length of pole) | height=20 #choose between 6.1 and 38.1 and represents the height of the poles | mu_a1 = [6.796,-0.01010,-0.06515,0.00616,-0.06736,0.00003251,-0.001243, 0.004034,-0.0000005851,-0.00001203, -0.0001332,0.0002266, 0.001649,-0.0000521,0.0005313]; mu1 = mu_a1[0] + (mu_a1[1] * wind_direction) + (mu_a1[2]*conductor_area) + (mu_a1[3]*age) + (mu_a[4]*height) +(mu_a1[5]*wind_direction**2) + (mu_a1[6]*conductor_area*wind_direction) + (mu_a1[7]*conductor_area**2) + (mu_a1[8]*age*wind_direction) +(mu_a1[9]*age*conductor_area) +(mu_a1[10] * age**2) + (mu_a1[11]*wind_direction*height) +(mu_a1[12]*conductor_area*height) + (mu_a1[13]*age*height) +(mu_a1[14]*height**2) | sigma_a1 = [0.1522,0.000111,0.0008277,-0.002052,0.0001701,-0.0000003334,0.000005995,-0.00004556,0.0000002687,0.000002605,0.00006349, -0.000002926,-0.00002166,0.000003454,0.000001269]; sigma1 = sigma_a1[0] + (sigma_a1[1] * wind_direction) + (sigma_a1[2]*conductor_area) + (sigma_a1[3]*age) + (sigma_a1[4]*height) +(sigma_a1[5]*wind_direction**2) + (sigma_a1[6]*conductor_area*wind_direction) + (sigma_a1[7]*conductor_area**2) + (sigma_a1[8]*age*wind_direction) +(sigma_a1[9]*age*conductor_area) +(sigma_a1[10] * age**2) + (sigma_a1[11]*wind_direction*height) +(sigma_a1[12]*conductor_area*height) + (sigma_a1[13]*age*height) +(sigma_a1[14]*height**2) |  | https://www.sciencedirect.com/science/article/pii/S0141029618327238
Wind Gust Speed (m/s) | Wood Utility Pole (class 7) | y | n | age=5 #choose between 0 and 101 | wind_direction=60 #choose between 0 and 90 degrees | conductor_area=3 #choose between 0 and 8 (calculated as a product of number and diameter of pole, span length of pole) | height=20 #choose between 6.1 and 38.1 and represents the height of the poles | mu_a7 = [6.478,-0.01502,-0.09623,0.006447,-0.05769,0.00006149,-0.001427,0.006283,0.00000453,0.00004580,-0.0001420,0.0002572,0.00181, -0.00002027,0.0004138]; mu7 = mu_a7[0] + (mu_a7[1] * wind_direction) + (mu_a7[2]*conductor_area) + (mu_a7[3]*age) + (mu_a7[4]*height) +(mu_a7[5]*wind_direction**2) + (mu_a7[6]*conductor_area*wind_direction) + (mu_a7[7]*conductor_area**2) + (mu_a7[8]*age*wind_direction) +(mu_a7[9]*age*conductor_area) +(mu_a7[10] * age**2) + (mu_a7[11]*wind_direction*height) +(mu_a7[12]*conductor_area*height) + (mu_a7[13]*age*height) +(mu_a7[14]*height**2) | sigma_a7=[0.1288,5.202E-04,4.527E-03,-1.592E-03,2.546E-04,-6.594E-08,-1.995E-05,-1.031E-04,-7.959E-06, -6.315E-05,6.677E-05,-4.626E-06,-1.984E-05,1.023E-05,-1.726E-06]; sigma7 = sigma_a7[0] + (sigma_a7[1] * wind_direction) + (sigma_a7[2]*conductor_area) + (sigma_a7[3]*age) + (sigma_a7[4]*height) +(sigma_a7[5]*wind_direction**2) + (sigma_a7[6]*conductor_area*wind_direction) + (sigma_a7[7]*conductor_area**2) + (sigma_a7[8]*age*wind_direction) +(sigma_a7[9]*age*conductor_area) +(sigma_a7[10] * age**2) + (sigma_a7[11]*wind_direction*height) +(sigma_a7[12]*conductor_area*height) + (sigma_a7[13]*age*height) +(sigma_a7[14]*height**2) |  | https://www.sciencedirect.com/science/article/pii/S0141029618327238
Wind Gust Speed (m/s) | New Wood Utility Pole | y | y |  |  |  |  | 4.0603 | 0.114 |  | https://www.tandfonline.com/doi/full/10.1080/15732479.2015.1053949#d1e662
| New Steel Utility Pole | y | y |  |  |  |  | 4.064 | 0.126
| Wood Pole 40 Years | y | y |  |  |  |  | 4.024 | 0.146
| Steel Pole 40 Years | y | y |  |  |  |  | 3.91 | 0.13
| Wood Pole 60 Years | y | y |  |  |  |  | 3.93 | 0.2023
| Steel Pole 60 Years | y | y |  |  |  |  | 3.892 | 0.129
Maximum Sustained Wind Speed (m/s) | Transmission Tower #1 | y | y | Wind speed angle = 0 |  |  |  | 3.916 | 0.0416 |  | https://www.sciencedirect.com/science/article/pii/S0141029621007367 | #VALUE!
|  | y | y | Wind speed angle = 30 |  |  |  | 3.873 | 0.0446
|  | y | y | Wind speed angle = 60 |  |  |  | 3.961 | 0.0509
| Transmission Tower #2 | y | y | Wind speed angle = 0 |  |  |  | 3.734 | 0.0546
|  | y | y | Wind speed angle = 30 |  |  |  | 3.789 | 0.0592
|  | y | y | Wind speed angle = 60 |  |  |  | 3.997 | 0.0474
Wind speed (m/s) (at top) | Steel Tower | y | y | Ice Thickness = 0mm |  |  |  | 3.628 | 0.1158 |  | Bilionis, D.V. and D. Vamvatsikos. 2019. Wind performance assessment of telecommunication towers: a case study in Greece. Proceedings of 7th interactional conference on computational methods in structural dynamics and earthquake engineering, COMPDYN 2019. pp. 5741-5755. https://files.eccomasproceedia.org/papers/compdyn-2019/19629.pdf?mtime=20191122132148
|  |  |  | Ice Thickness = 15 mm |  |  |  | 3.471 | 0.1151
|  |  |  | Ice Thickness = 30 mm |  |  |  | 3.448 | 0.127
|  |  |  | Ice Thickness =45 mm |  |  |  | 3.384 | 0.1225
Wind speed (m/s) | Wind Turbine Tower in Parked Condition | y | y | Critical Displacement = 0.524 m | [6 empty] | https://www.sciencedirect.com/science/article/pii/S0960148120311423?via%3Dihub#sec4
|  | y | y | Critical Displacement = 0.629 m
| Wind Turbine Blade 1 in Parked Condition | y | y | Critical Displacement = 0.524 m |  |  |  | 3.0343 | 0.118
|  | y | y | Critical Displacement = 0.629 m |  |  |  | 3.2248 | 0.119
|  | y | y | Critical Displacement = 0.839 m |  |  |  | 3.365 | 0.122
|  | y | y | Critical Displacement = 1.049 m |  |  |  | 3.6007 | 0.185
| Wind Turbine Blade 2 in Parked Condition | y | y | Critical Displacement = 0.524 m |  |  |  | 2.982 | 0.088
|  | y | y | Critical Displacement = 0.629 m |  |  |  | 3.815 | 0.522
|  | y | y | Critical Displacement = 0.839 m |  |  |  | 3.3176 | 0.1083
|  | y | y | Critical Displacement = 1.049 m |  |  |  | 3.6007 | 0.185
| Wind Turbine Tower in Operating Condition | y | y | Critical Displacement = 0.524 m |  |  |  | 2.853 | 0.246
|  | y | y | Critical Displacement = 0.629 m |  |  |  | 3.105 | 0.248
|  | y | y | Critical Displacement = 0.839 m |  |  |  | 3.497 | 0.247
|  | y | y | Critical Displacement = 1.049 m |  |  |  | 23.615 | 7.622
| Wind Turbine Blade 1 in Operating Condition | y | y | Critical Displacement = 0.524 m |  |  |  | 1.999 | 0.436
|  | y | y | Critical Displacement = 0.629 m |  |  |  | 2.8717 | 0.445
|  | y | y | Critical Displacement = 0.839 m |  |  |  | 3.487 | 0.435
|  | y | y | Critical Displacement = 1.049 m |  |  |  | 4.006 | 0.455
| Wind Turbine Blade 2 in Operating Condition | y | y | Critical Displacement = 0.524 m |  |  |  | 1.763 | 0.457
|  | y | y | Critical Displacement = 0.629 m |  |  |  | 2.782 | 0.451
|  | y | y | Critical Displacement = 0.839 m |  |  |  | 3.517 | 0.469
|  | y | y | Critical Displacement = 1.049 m |  |  |  | 4.285 | 0.567
| Wind Turbine Blade 3 in Operating Condition | y | y | Critical Displacement = 0.524 m |  |  |  | 1.701 | 0.51
|  | y | y | Critical Displacement = 0.629 m |  |  |  | 2.795 | 0.499
|  | y | y | Critical Displacement = 0.839 m |  |  |  | 3.579 | 0.517
|  | y | y | Critical Displacement = 1.049 m |  |  |  | 4.791 | 0.821

## Snow
Hazard Variable | Infrastructure Component | Lognormal Distribution (y/n) | Best Fit (y/n) | 1st Additional Variables | 2nd Additional Vriable | 3rd Additional Variable | 4th Additional Variable | Mu (if lognormal distribution) | Sigma (if lognormal distribution) | Alternate Equation | Source
Ice Thickness (mm) | Transmission Tower | y | y | Uniform balance load | no wind |  |  | 4.223 | 0.0376 |  | https://open.library.ubc.ca/soa/cIRcle/collections/53032/items/1.0076203
|  |  |  | Longitudinal Bending |  |  |  | 4.293 | 0.0422
|  |  |  | Traverse Bending |  |  |  | 4.255 | 0.0384
|  |  |  | Torsional Bending |  |  |  | 4.273 | 0.0409
|  |  |  | Uniform balance load | wind=20m/s | wind direction=0deg |  | 4.258 | 0.0273
|  |  |  | Longitudinal Bending |  |  |  | 4.653 | 0.0527
|  |  |  | Traverse Bending |  |  |  | 4.297 | 0.0373
|  |  |  | Torsional Bending |  |  |  | 4.332 | 0.0567
|  |  |  | Uniform balance load | wind=20m/s | wind direction=90deg |  | 4.252 | 0.0208
|  |  |  | Longitudinal Bending |  |  |  | 4.252 | 0.0208
|  |  |  | Traverse Bending |  |  |  | 4.252 | 0.0208
|  |  |  | Torsional Bending |  |  |  | 4.252 | 0.0208

## Heat
Hazard Variable | Infrastructure Component | Lognormal Distribution (y/n) | Best Fit (y/n) | 1st Additional Variables | 2nd Additional Vriable | 3rd Additional Variable | 4th Additional Variable | Mu (if lognormal distribution) | Sigma (if lognormal distribution) | Alternate Equation | Source
Temperature (degC) | Cables: Thermoplastic Insulation | y | n |  |  |  |  | 5.52 | 0.117 |  | https://link.springer.com/article/10.1007/s10694-016-0616-0#Tab3
| Cables: Thermoset Insulation | y | n |  |  |  |  | 6.04 | 0.0516
| Cables: Kerite-FR | y | n |  |  |  |  | 5.93 | 0.141

## Flood
Hazard Variable | Infrastructure Component | Lognormal Distribution (y/n) | Best Fit (y/n) | 1st Additional Variables | 2nd Additional Vriable | 3rd Additional Variable | 4th Additional Variable | Mu (if lognormal distribution) | Sigma (if lognormal distribution) | Alternate Equation | Source
Depth of flood (ft) | Solar PV Panel | y | y |  |  |  |  | 3.1098 | 1.3335 |  | B Chen. 2020. “Optimization framework for solar energy integrated resilient distribution grid.” Argonne National Laboratory CPS#34228- Final Project Review. http://wzy.ece.iastate.edu/project/34228_FPRANL_v0.4.pdf
| Solar Substation | y | y |  |  |  |  | 4.6245 | 2.1871
| Pole | y | y |  |  |  |  | 7.4385 | 2.5546
Depth of flood (m) | High Voltage Substation | y | y |  |  |  |  | 0.3572 | 0.4759 |  | D Sánchez-Muñoz, J L Domínguez-García , E Martínez-Gomariz, B Russo, J Stevens, and M Pardo. 2020. "Electrical Grid Risk Assessment Against Flooding in Barcelona and Bristol Cities" Sustainability 12- 4(2020) 1527.. https://doi.org/10.3390/su12041527
| Medium Voltage substation | y | y |  |  |  |  | 0.4197 | 0.1745